## Parameters
Component | Variable Name | Value | Units | Description | Source ID | Notes | To-do
Price Profile | fname_price | N/A | $/MWh | path for the CSV filename pointing to the energy price profile csv file | [1], [2] | This filename changes based on the price profile input
Representative Weeks | fname_w | N/A | <string> | path for filename pointing to the weights of the clustered price profile |  | This filename changes based on the associated price profile input, and is conditional on if this uses representative weeks
| fname_map | N/A | <string> | path for the filename pointing to the mapping of clusters to each week in the year |  | This filename changes based on the associated price profile input, and is conditional on if this uses representative weeks
| fname_modeled_indices | N/A | <string> | path for the filename pointing to the indices of the weeks in the year that are centroids of the representative weeks |  | This filename changes based on the associated price profile input, and is conditional on if this uses representative weeks
| W | 52 | weeks | Number of weeks in the year |  | conditional on if this uses representative weeks
| T | 168 | hours | Number of hours in a week |  | conditional on if this uses representative weeks
| N | 23 | weeks | Number of representative weeks |  | 23 representative weeks were chosen, because it best represented the original hourly price profile compared to using 5 to 25 representative weeks
Coal Plant | flowSteam_peak | 0.445 | tonne/s | peak steam flow rate, set by coal plant datasheets | [3], [4], [5]
| Tsteam_peak | 540 | C | peak steam temperature | [3],[4]
| minpower_fraction | 0.17 | [0 - 1] | minimum power fraction, set by the original coal plant | [6], [7]
| start_up_fuel | 4.1032 | MWh per MW | coal plant start up fuel for large subcritical plant (14 MMBtu / MW capacity) | [8]
| start_cost | 0.01015 | $1k/MW | cold start-up cost, associated with the start-up costs from auxiliary power consumption, water chemistry and other non-fuel expenditures documented by coal plants | [8], [20], [34] | Based off start up costs for CSP facility, which are 10% of coal plants. Coal plants cold start up costs not including fuel start up costs are in the range of 10.15 to $11.58 / MW 6520 $/start for a 163 MW x 2 hybrid CSP system | 5.075
| powerPeak | 500 | MW | interconnection capacity, set by the original facility | [4], [12], [13] | interchangable with dischargepowerPeak
| chargerpowerPeak | 500 | MW | interconnection capacity, set by the original facility | [4], [12], [13]
| ramp_rate_min | 0.5 | [0 - 1] | ramp rate as % per hour, set by the original coal plant | [4], [12], [13]
| coal_FOM | 31.564 | $1k/MW_e/year | Annual fixed operating cost per MW_e for subcritical unit in 2030 (supercritical is 0.2 cr/MW/year) | [4] , [31]
| emissions_rate | 0 | tonnes / MWh | Emissions rate of coal plant (not applied) | [3] | (0.778 for Trombay)
| coal_fuel_cost | 0.047715 | $1k/MWh | Fuel cost of coal calculated from CEEW data | [4] | Fuel cost of coal (=(15000/BESS!K4)*0.8 /1000) this uses the 15000 Rs per ton given by Tata Power | check with CEEW & Trombay notes, add calcs to this spreadsheet
| coal_VOM | 0.09712 | $1k / MWh | Variable operating cost of the coal plant | [4] |  | check with CEEW & Trombay notes, add calcs to this spreadsheet
| upgrade_cost | 0 | $1k | cost toward upgrading the coal plant to extend the life of the steam-turbine power block if it needs upgrades | [28]
| life | 25 | years | remaining lifetime of the existing infrastructure, in years | [4], [12], [13]
Salt Characteristics | T_hot | 840 | K | Temperature of the hot salt | [9] | Characteristics for Solar Salt (NaNO3:KNO3) at 60:40 ratio
| T_cold | 563 | K | Temperature of the cold salt | [9] | Characteristics for Solar Salt (NaNO3:KNO3) at 60:40 ratio
| cp | 1.56 | MJ/tonne-K (kJ/kgK) | heat capacity of the salt | [9], [10] | Characteristics for Solar Salt (NaNO3:KNO3) at 60:40 ratio
Storage Tank | cost_tank | 20.2268 | $1k/MWh_t | calculated parameter, in 1000 USD per MWh thermal | [9],[10],[11],[17],[14],[15],[16] | Reference "Calculation tank cost"
| min_hours | 0 | hours | minimum hours of storage
| alpha_hot | 0.00041667 | [0 - 1] | self discharge rate per hour for the thermal storage system (1% per day) | [22]
Storage Component: Heat Exchanger | c_base | 4000 | $1k | base heat exchanger costs derived, calculations in "Calculation heat exchanger" sheet | [19]
| UA_base | 3.0807 | MJ/s-K | base UA value derived, calculations in "Calculation heat exchanger" sheet | [19]
| n_HX | 0.6 | [0-1] | cost relationship | [9]
| UA_step | 0.5 | MJ/s-K | step size for piecewize linearization constraint
| Q_loss | 0.03 | [0 - 1] | percentage of energy dissapated in heat exchanger, percentage of power output | [22]
Storage Component: Salt Pumps | pipes_valves_cost | 4.6619 | $1k/MW_e | see calculations in "Calculation tank cost" sheet. Scales with power output | [11]
| hotpump_slope | 1.4339 | $1k/kW_e | see calculations in "Calculation salt pumps" sheet | [23]
| hotpump_intercept | 154.729 | $1k | see calculations in "Calculation salt pumps" sheet | [23]
| h | 15 | m | head | [24]
| g | 9.81 | m/s^2 | gravitational constant
| pump_eff | 0.75 | [0 - 1] | efficiency of the pump | [24]
| coldpump_slope | 0.47501 | $1k/kW_e | see calculations in "Calculation salt pumps" sheet | [23]
| coldpump_intercept | 200.566 | $1k | see calculations in "Calculation salt pumps" sheet | [23]
Charger | cost_charger | 1.815 | $1k/MW_th | cost of the resistive heater | [25]
| beta | 0.95 | [0 - 1] | efficiency of the resistive heater | [25]
Aspen Outputs: Molten Salt Retrofit | deltaT_A | 25 | K | Temperature difference of two streams (steam and salt flows) at at end A in countercurrent heat exchanger. Calculations in "Calculations Aspen" sheet | [26]
| deltaT_B | 240 | K | Temperature difference between two streams (steam and salt flows) at end B in countercurrent heat exchanger. Calculations in "Calculations Aspen" sheet | [26]
| steam_eff | 0.35811 | [0 - 1] | efficiency of steam turbine calculated by net power output divided by heat input from salt flow rate | [26]
| Q_s | 3405.9965 | MJ/tonne | enthalpy change of the steam | [26]
Other | TES_FOM | 0 | $1k / MW-year | Fixed operating and maintenance costs of TES. Calculated from "Upgrade Costs" tab which uses generic CSP literature (85.39 $1k/MWh is larger than the coal plant FOM) | [28] |  | need to change this based on labor differences
| TES_VOM | 0.0010491 | $1k / MWh | VOM from water usage , scaling with dispatch | [3]
| ir | 0.09 | [0-1] | India's inflation rate | [27]
| syn_con_rating | 0.35 | MVArh/MW | VAR support per MW of installed capacity (unused) | [30]
| syn_con_comp | 2e-05 | $/kVARh | compensation for VARS (unused) | [30]
| carbon_price | 0.05 | $1k / tonne | Price of carbon
| M | 6000 | N/A | modeling parameter (big M notation)
Optional: Regulatory Incentives | gbi_subsidy | 0 | $1k/MWh_e | Generation Based Incentives - subsidy per MWh of electricity produced
| taxcredit | 0 | [0 - 1] | Tax Credit amount, applied to capital cost
Optional: Industrial Co-production | x | 0 | [0 - 1] | percentage of maximum rated power of power plant that goes to industrial load |  | Q_ind, the industrial load, is set in the model script by Q_ind = x*powerPeak
| cost_heater | 1.815 | $1k/MW_t | cost of the heater per MW input, equivalent to the cost of the resistive heater | [25]
| beta_1 | 7.384 | N/A | coefficients for characterizing power and efficiency relationship given industrial demand
| beta_2 | 1.31 | N/A | coefficients for characterizing power and efficiency relationship given industrial demand
| beta_3 | 0.5279 | N/A | coefficients for characterizing power and efficiency relationship given industrial demand

## Calculation tank cost
Model Input | Variable Name | Value | Units | Description | Source ID | Notes
Storage Tank
| tank_insulation | 235 | $/m2 | cost of tank insulation, which applies to the surface area of 2 cylindrical tanks | [9] |  | Reference System [11] |  |  | Table 1: Component costs for direct, two-tank molten salt TES system (base case) [11]
| tank_foundation | 1210 | $/m2 | cost of tank foundation, which applies just to the bottom area of the tank | [9] |  | Power Output | 100 | MW_e | Component | Total Cost (Materials + Installation Costs, in $/kWh_th) in 2011 | Total Cost (Materials + Installation Costs, in $/kWh_th) in 2023 USD
| hottank_material | 6.56 | $/kg | cost of tank shell material (stainless steel), which applies to the entire surface area at a specified design thickness | [9], [11] |  | Rankine System Efficiency | 0.45 | [0 - 1] | High-temperature tank - stainless steel | 7.04 | 9.4228
| coldtank_material | 0.56 | $/kg | cost of tank shell material (carbon steel), which applies to the entire surface area at a specified design thickness | [9], [11] |  | Storage Hours | 6 | hours | Low-temperature tank - carbon steel | 3.14 | 4.2028
| solar_salt | 1.3 | $/kg | cost of the solar salt storage material | [9], [10], [11] | Characteristics for Solar Salt (NaNO3:KNO3) at 60:40 ratio |  |  |  | Tank supports, foundations, and site work | 2.65 | 3.5469
| salt_density | 1835.6 | kg/m3 | salt density | [9], [10], [16] | Characteristics for Solar Salt (NaNO3:KNO3) at 60:40 ratio | Assumptions | Value | Source | Storage Medium | 12.1 | 16.1954
| hottank_shell_density | 7959.5 | kg/m3 | density of hot tank shell material | [9], [17] |  | CPI in 2023 | 127.02 | [14] | Electrical and Instrumentation | 0.9 | 1.2046
| coldtank_shell_density | 7850 | kg/m3 | density of cold tank shell material (carbon steel) | [17] |  | CPI in 2011 | 94.9 | [14] | Pipes,valves, and fittings | 0.39 | 0.522
| delta | 0.00635 | m | design thickness of shells | [15]
| h_0 | 12 | m | maximum tank height | [15]
Calculations
| deltaT | 277 | K | temperature difference of the hot salt and cold salt
| cp | 1.56 | kJ/kgK | specific heat capacity of solar salt
| h_1 | 12.0063 | m | total height including the design thickness of the shell
| n_tanks | 2 | tanks | number of tanks |  |  |  | Value | Source
| MWh_t | 1 | MWh_t | adjustable input
| Q | 3600000 | kJ | thermal capacity (variable) which is equal to 1000 MWh_t |  |  | Reference Temperature (Celcius) | 400 | Using reference temperature from [16]
| m_s | 4165.5096 | kg | kg of salt per tank |  |  | Calculating density at reference temperature (kg/m3) | 1835.6 | Calculated using equation from [10]
| r_0 | 0.24535 | m | inner radius of one tank |  |  | Density of stainless steel 304 (kg/m3) | 7930 | [17]
| r_1 | 0.2517 | m | outer radius of one tank |  |  | Density of stainless steel 316 (kg/m3) | 7989 | [17]
| area_insulation | 18.6878 | m2 | area of one tank insulation |  |  | Calculating Density of hot tank material (kg/m3) | 7959.5 | Calculated the average
| area_foundation | 0.2534 | m2 | area of one tank foundation material (square)
| V_shell | 0.12278 | m3 | volume of the cylindrical shell
| m_cold_shell | 1.5641e-05 | kg | mass of cold tank material
| m_hot_shell | 1.5425e-05 | kg | mass of hot tank material
| cost_coldtank | 10113.4101 | $ | cost of the cold tank given Q
| cost_hottank | 10113.4102 | $ | cost of hot tank given Q
| cost_tank | 20226.8202 | $ | total cost of tanks given Q
| Final Calculation for cost_tank | 20.2268 | $1k/MWh_t | value for cost_tank parameter in "Parameters" sheet
| Final Calculation for pipes and valves costs | 4.6619 | $1k/MW_e | value for pipes_valves_cost in "Parameters" sheet
| footprint with buffer | 660.3457 | m2 | for both tanks with 10 m buffer | [33]
percentage breakdown
|  | 0.53544 | material
|  | 0.46456 | tank related components
Checking Linearity
| MWh_t | total cost ($1k)
| 200 | 2423
| 1000 | 11777
| 3000 | 34983
| 4000 | 46559

## Calculation heat exchanger
Model Input | Variable Name | Value | Units | Description | Source ID | Notes
Storage Component: Heat Exchanger
| steam_temp_low | 50 | Celcius | input steam temperature for supercritical Rankine system | [19] | 241.7
| steam_temp_high | 550 | Celcius | peak steam temperature for supercritical Rankine system | [19] | 550
| salt_temp_high | 565 | Celcius | minimum temperature of salt (solar salt mixture) | [19] | 679
| salt_temp_low | 290 | Celcius | maximum temperature of salt (solar salt mixture) | [19] | 586
| Duty | 3400 | MW_t = MJ/s | one shell and tube heat exchanger | [19]
| CPI ratio | 1.3688 |  | CPI in 2023/CPI in 2010 | [21]
| U | 3804.16 | W/m^2 K | Supercritical Rankine Cycle overall heat T/F coefficient for KF-ZrF4 secondary heat exchanger
| A | 4871.92 | m^2 | Supercritical Rankine Cycle heat T/F surface area for KF-ZrF4 secondary heat exchanger
| unit_cost_MS | 4000000 | $ | molten salt HX cost for 1000 MWh_t system | [9]
| unit_cost | 301693000 | $ | one shell and tube heat exchanger total cost in USD 2010 | [19]
Calculations | [6 empty] | power_out | 510 | 930 | MW | Notes
| deltaT_A | 15 | K | temperature difference between two streams at end A |  |  | deltaT_LM | 218.8805 | 218.8805 | K
| deltaT_B | 240 | K | temperature difference between two streams at end B |  |  | UA | 6.6573 | 12.1397 | MW/K
| deltaT_LM | 81.1516 | K | log mean temperature difference of the heat exchanger |  |  | c_hx | 6351134.1181 | 9107495.1237 | $
| UA_base_1 | 41.8969 | MW_t/K | used to estimate the UA_base for KF-ZrF4 | [19] |  | unit_cost | 12453.2042 | 9793.0055 | $/MW | This 100x higher than the $4000 / MWh_t that Jacobs 2017 cites [9]
Final Calculations | c_base | 4000 | $1k | $1k in USD 2023 | [9]
| UA_base | 3.0807 | MW/K | UA value associated with this particular heat exchanger | [9]

## Calculation salt pumps
Model Input | Variable Name | Value | Units | Description | Source ID | Notes | cost hot pump ($) | cost cold pump ($) | hot pump rated power (kW_e) | cold pump rated power (kW_e) | hot pump unit cost ($/kW_e) | cold pump unit cost ($/kW_e) | hot pump ($/MW_e) | cold pump ($/MW_e)
Calculations for Salt Pumps | [6 empty] | 577300.046 | 233007.1844 | 300 | 150 | 1924.3335 | 1553.3812 | 1374.7892 | 3437.7904
| hotpump_slope | 1.4339 | $1k/kW_e |  | [23] |  | 608497.8054 | 249649.819 | 320 | 170 | 1901.5556 | 1468.5283 | 1358.5162 | 3250.0024
| hotpump_intercept | 154.729 | $1k |  | [23] |  | 639337.6285 | 265434.1486 | 340 | 190 | 1880.4048 | 1397.0218 | 1343.4055 | 3091.7512
| coldpump_slope | 0.47501 | $1k/kW_e |  | [23] |  | 669844.3496 | 280488.5164 | 360 | 210 | 1860.6787 | 1335.6596 | 1329.3127 | 2955.9503
| coldpump_intercept | 200.566 | $1k |  | [23] |  | 700039.7998 | 294911.8294 | 380 | 230 | 1842.21 | 1282.2253 | 1316.1182 | 2837.6949
[7 empty] | 729943.3087 | 308782.2609 | 400 | 250 | 1824.8583 | 1235.129 | 1303.7217 | 2733.466
[7 empty] | 759572.1018 | 322162.8932 | 420 | 270 | 1808.505 | 1193.1959 | 1292.0386 | 2640.6637
Calculations for Cost of Heater | [6 empty] | 788941.6183 | 335105.5236 | 440 | 290 | 1793.0491 | 1155.5363 | 1280.9965 | 2557.3192
| Charging capital cost | 3.3 | $/kW_e | cost of resistive heater in kW_e | [25] |  | 818065.7693 | 347653.3156 | 460 | 310 | 1778.4038 | 1121.4623 | 1270.5336 | 2481.91
| Efficiency down | 0.55 | [0 - 1] | efficiency down fraction | [25] |  | 846957.1486 | 359842.6975 | 480 | 330 | 1764.4941 | 1090.4324 | 1260.5961 | 2413.2377
| Converted charging capital cost | 1.815 | $1k/MW_th | Convert the charging capital cost by multiplying by the discharge efficiency and scale to match the units | [25] |  | 875627.2074 | 371704.7544 | 500 | 350 | 1751.2544 | 1062.0136 | 1251.1374 | 2350.3439
[7 empty] | 904086.3986 | 383266.2702 | 520 | 370 | 1738.6277 | 1035.8548 | 1242.1166 | 2292.4518
[7 empty] | 932344.3 | 394550.5212 | 540 | 390 | 1726.5635 | 1011.668 | 1233.4977 | 2238.924
[7 empty] | 960409.7159 | 405577.8903 | 560 | 410 | 1715.0173 | 989.2144 | 1225.2488 | 2189.2319
[7 empty] | 988290.7661 | 416366.3494 | 580 | 430 | 1703.9496 | 968.2938 | 1217.3417 | 2142.9326
[7 empty] | 1015994.96 | 426931.8424 | 600 | 450 | 1693.3249 | 948.7374 | 1209.7512 | 2099.6523
[7 empty] | 1043529.2618 | 437288.5937 | 620 | 470 | 1683.1117 | 930.4013 | 1202.4547 | 2059.0725
[7 empty] | 1070900.1458 | 447449.358 | 640 | 490 | 1673.2815 | 913.162 | 1195.4317 | 2020.9201
[7 empty] | 1098113.6457 | 457425.626 | 660 | 510 | 1663.8086 | 896.913 | 1188.664 | 1984.9595
[7 empty] | 1125175.3966 | 467227.7935 | 680 | 530 | 1654.6697 | 881.5619 | 1182.135 | 1950.986
[7 empty] | 1152090.6725 | 476865.3034 | 700 | 550 | 1645.8438 | 867.0278 | 1175.8296 | 1918.8206
[7 empty] | 1178864.4188 | 486346.7639 | 720 | 570 | 1637.3117 | 853.2399 | 1169.7341 | 1888.3066 | Sizing for TX coal plants
[7 empty] | 1205501.2814 | 495680.0488 | 740 | 590 | 1629.0558 | 840.1357 | 1163.8358 | 1859.3056 | capsize | 510 | MW | 930
[7 empty] | 1232005.6327 | 504872.383 | 760 | 610 | 1621.06 | 827.6596 | 1158.1235 | 1831.6949 | hot pump sub | 713.8622 | kWe | 1139.0302
[7 empty] | 1258381.5941 | 513930.4154 | 780 | 630 | 1613.3097 | 815.7626 | 1152.5865 | 1805.3654 | cold pump sub | 230.4458 | kWe | 420.2247
[7 empty] | 1284633.0568 | 522860.2813 | 800 | 650 | 1605.7913 | 804.4004 | 1147.2152 | 1780.2199 | 1259.697 | 2459.4324
[7 empty] | 1310763.6997 | 531667.6565 | 820 | 670 | 1598.4923 | 793.5338 | 1142.0006 | 1756.1709
[7 empty] | 1336777.0062 | 540357.8049 | 840 | 690 | 1591.4012 | 783.1273 | 1136.9345 | 1733.1401
[7 empty] | 1362676.2789 | 548935.6189 | 860 | 710 | 1584.5073 | 773.1488 | 1132.0094 | 1711.0567
[7 empty] | 1388464.6527 | 557405.6551 | 880 | 730 | 1577.8007 | 763.5694 | 1127.218 | 1689.8566
[7 empty] | 1414145.1075 | 565772.1666 | 900 | 750 | 1571.2723 | 754.3629 | 1122.554 | 1669.4817
[7 empty] | 1439720.4786 | 574039.1302 | 920 | 770 | 1564.9136 | 745.5054 | 1118.0111 | 1649.8791
[7 empty] | 1465193.4668 | 582210.271 | 940 | 790 | 1558.7165 | 736.975 | 1113.5838 | 1631.0006
[7 empty] | 1490566.6478 | 590289.0845 | 960 | 810 | 1552.6736 | 728.752 | 1109.2666 | 1612.8021
[7 empty] | 1515842.4802 | 598278.856 | 980 | 830 | 1546.778 | 720.8179 | 1105.0547 | 1595.2432
[7 empty] | 1541023.313 | 606182.6778 | 1000 | 850 | 1541.0233 | 713.1561 | 1100.9434 | 1578.2869
[7 empty] | 1566111.3931 | 614003.4651 | 1020 | 870 | 1535.4033 | 705.7511 | 1096.9283 | 1561.8989
[7 empty] | 1591108.871 | 621743.9696 | 1040 | 890 | 1529.9124 | 698.5887 | 1093.0054 | 1546.0478
[7 empty] | 1616017.8072 | 629406.7925 | 1060 | 910 | 1524.5451 | 691.6558 | 1089.1709 | 1530.7046
[7 empty] | 1640840.1771 | 636994.3955 | 1080 | 930 | 1519.2965 | 684.9402 | 1085.4212 | 1515.8422
[7 empty] | 1665577.8768 | 644509.1113 | 1100 | 950 | 1514.1617 | 678.4306 | 1081.7528 | 1501.4359
[7 empty] | 1690232.7268 | 651953.1529 | 1120 | 970 | 1509.1364 | 672.1167 | 1078.1626 | 1487.4624
[7 empty] | 1714806.4768 | 659328.622 | 1140 | 990 | 1504.2162 | 665.9885 | 1074.6475 | 1473.9002
[7 empty] | 1739300.8096 | 666637.517 | 1160 | 1010 | 1499.3972 | 660.0371 | 1071.2047 | 1460.7292
[7 empty] | 1763717.3447 | 673881.7395 | 1180 | 1030 | 1494.6757 | 654.2541 | 1067.8315 | 1447.9308
[7 empty] | 1788057.6417 | 681063.1013 | 1200 | 1050 | 1490.048 | 648.6315 | 1064.5254 | 1435.4874
[7 empty] | 1812323.2034 | 688183.3298 | 1220 | 1070 | 1485.5108 | 643.162 | 1061.2839 | 1423.3828
[7 empty] | 1836515.4791 | 695244.0738 | 1240 | 1090 | 1481.0609 | 637.8386 | 1058.1048 | 1411.6016

## Calculation Upgrade Costs
Variable Name |  | Units | Description | Source ID
TES | 65276000 | $ | Direct costs based on EPC contracting approach. Include equipment, material, and labor to construct. | [28] from CSP
Balance of Plant | 36413000 | $ | Direct costs based on EPC contracting approach. Include equipment, material, and labor to construct. | [28] from CSP
Power Block (steam turbine, steam cycle, related systems) | 122077000 | $ | Direct costs based on EPC contracting approach. Include equipment, material, and labor to construct. | [28] from CSP
Land | 1 | $/kW | Direct costs based on EPC contracting approach. Include equipment, material, and labor to construct. | [3] |  |  |  |  | Notes
Electrical Interconnection | 1200000 | $ | Direct costs based on EPC contracting approach. Include equipment, material, and labor to construct. | [28] from CSP |  | Greenfield TES Discharge Inv. | 1596900.01 | $/MW discharge | 100 x difference from TES retrofits in India
P_out | 100 | MW | 115 gross MW | [28] from CSP |  | Greenfield TES Energy Inv | 81595 | $/MWh | 4x difference
hours | 8 | hours |  | [28] from CSP |  | Percentage of Greenfield | 0.3 |  | random factor to play with
FOM | 85.39 | $/kW-year | labor, materials, utilities, contracted services, G&A costs. Exclude property costs and insurance | [28] from CSP |  | Retrofit Discharge Inv (upgrades) | 366231 | $/MW | 10 x difference from retrofits, includes U.S. labor costs
VOM | 0 | $/MWh | all costs tied to energy produced are covered in fixed cost | [28] from CSP |  | Retrofit Energy Inv | 81595 | $/MWh | 4 x
BESS_capex_kW | 845 | $/kW-net | capital cost of 50 MW, 100 MWh, 2 hour battery | [28] Battery Energy System | used for comparison
BESS_capex_kWh | 423 | $/kWh | capital cost of 50 MW, 100 MWh, 2 hour battery | [28] Battery Energy System | used for comparison
Calculations
Greenfield_TES | 2250.66 | $1k / MW_e | $1k per MW power output
Upgrade_costs | 1220.77 | $1k / MW_e | $1k per MW power output
FOM | 10673.75 | $/MWh-year for GenX input
TES_FOM | 85.39 | $1k / MW_e for TES parameters input

## Calculations Aspen
Model Input | Variable Name | Value | Units | Description | Source ID | Notes | Variable Name | Subcritical | Supercritical | Units | Description | Source ID
Aspen Results | [6 empty] | P_aux | 500 | 500 | kWe | auxiliary power consumption of the baseline subcritical modeled plant in NETL study | [3], Case B11A, B12A
Steam Flow | steam_flow | 385 | kg/s | flow rate of steam | [26] |  | X_loss | 2150 | 2150 | kWe | transformer losses in baseline subcrtical modled plant in NETL study | [3], Case B11A, B12A | [6 empty] | Main Steam Characteristics |  |  |  |  | Calculations
| steam_peak_temp | 540 | C | peak temperature of steam | [26] |  | P_out | 687 | 685 | MWe | gross power output | [3], Case B11A, B12A |  |  | Load (MW) | Gross Heat Rate (kcal/kWh) | Turbine Heat Rate (kcal/kWh) | Boiler Efficiency (%) | Flow (kg/s) | Temperature (°C) | Pressure (MPa) | Condenser Vacuum (MPa) | Auxiliary Power Cons. (%) | Steam turbine efficiency | Aux Power in TES (MW) | Source
| T_low | 50 | C | lowest temperature of steam | [26] |  | P_aux_total | 37 | 35 | MWe | total aux power demand | [3], Case B11A, B12A | 500 MW | Average Design Values | 500 | 2254.6 | 1976.4 | 87.66 | 421.6111 | 537.6 | 16.7991 | 0.092428 | 7.84 | 0.43513 | 1.9343 | [29]
| h_steam_1 | -15840779.5 | J/kg | enthalpy at peak temperature | [26] |  | c_feedwater | 25 | 25 | $/kW | overnight capital cost of feedwater system, including labor costs | [3], Case B11A, B12A |  | Average Operating Values | 446.3 | 2566.2 | 2109.1 | 82.21 | 370.2222 | 539.2 | 16.0341 | 0.088575 | 7.84 | 0.40776 |  | [29] | 3692.5279
| h_steam_2 | -12434783 | J/kg | enthalpy at lowest temepratuare | [26] |  | c_waterpretreat | 22 | 21 | $/kW | water makeup & pretreating | [3], Case B11A, B12A |  | Average Deviations (%) | 10.7% | 13.8% | 6.7% | -6.2% | -12.2% | 0.3% | -4.5% | -4.1% |  |  |  | [29]
Power | w_1 | -121814416 | W | Power from high pressure turbine | [26] |  | c_feedwatersub | 8 | 9 | $/kW | other feedwater subsystems | [3], Case B11A, B12A | 250 MW | Average Design Values | 250 | 2300.7 | 2004.2 | 87.18 | 207.8611 | 537.6 | 14.769 | 0.090921 | 9.44 | 0.4291 |  | [29]
| w_2 | -177080154 | W | Power from intermediate pressure turbine | [26] |  | c_servicewater | 37 | 35 | $/kW | service water systems | [3], Case B11A, B12A |  | Average Operating Values | 251.3 | 2687.2 | 2239.9 | 83.38 | 216.8333 | 537 | 14.7887 | 0.088228 | 9.44 | 0.38395 |  | [29]
| w_3 | -220572886 | W | Power from low pressure turbine | [26] |  | c_wastewatertreatment | 30 | 28 | $/kW | waste water treatment equipment | [3], Case B11A, B12A |  | Average Deviations (%) | 0.5% | 16.8% | 11.7% | -4.4% | 4.3% | -0.1% | 0.2% | -3% |  |  |  | [29]
| w_pump | 7387185.57 | W | Auxiliary Power Consumption | [26] |  | c_misc | 1 | 1 | $/kW | miscellaneous plant equipment | [3], Case B11A, B12A | 210 MW | Average Design Values | 210.1 | 2361.6 | 2025.5 | 85.8 | 179.1944 | 537.3 | 13.9453 | 0.091521 | 9.57 | 0.42459 | 0.81241 | [29]
Salt Flow | F_salt | 4200 | kg/s | flow rate of salt | [26] |  | c_steamturbine | 139 | 156 | $/kW | Steam Turbine Generator & accessories | [3], Case B11A, B12A |  | Average Operating Values | 198.5 | 2714.4 | 2213.8 | 81.7 | 174.0556 | 535 | 13.2196 | 0.087895 | 9.57 | 0.38847 |  | [29]
| max_temp | 565 | C | peak temperature of salt | [26] |  | c_steamturbineaux | 9 | 10 | $/kW | Steam Turbine Plant Auxiliaries | [3], Case B11A, B12A |  | Average Deviations (%) | -5.5 | 14.9 | 9.3 | -4.8 | -2.9 | -0.4 | -5.2 | -4 |  |  |  | [29]
| min_temp | 290 | C | lowest temperature of salt | [26] |  | c_condenseraux | 42 | 39 | $/kW | Condenser & Auxiliaries | [3], Case B11A, B12A | 195 - 200 MW | Average Design Values | 199 | 2399.6 | 2051.6 | 86.02 | 178.4167 | 538 | 13.3078 | 0.091988 | 10.24 | 0.41919 |  | [29]
| h_1 | -550612.565 | J/kg | enthalpy at peak temperature | [26] |  | c_steampiping | 93 | 106 | $/kW | Steam Piping | [3], Case B11A, B12A |  | Average Operating Values | 166.2 | 2989.1 | 2367.9 | 79.9 | 150.5278 | 532.8 | 10.7188 | 0.089108 | 10.24 | 0.36319 |  | [29]
| h_2 | -210144.155 | J/kg | enthalpy at lowest temperature | [26] |  | c_foundation | 1 | 1 | $/kW | Turbine Generator Foundations | [3], Case B11A, B12A |  | Average Deviations (%) | -16.4% | 24.4% | 15.4% | -7.1% | -14.5% | -1% | -19.6% | -3.1% |  |  |  | [29]
Calculations | [6 empty] | c_coolingtower | 37 | 35 | $/kW | cooling towers | [3], Case B11A, B12A | 140 MW | Average Design Values | 140.1 | 2381.2 | 2054 | 86.01 | 113.5833 | 539 | 13.0234 | 0.091095 | 12.83 | 0.4187 |  | [29]
| Q_in | 1429.9673 | MW input | salt mass flow [kg/s] * enthalpy change [J/kg] = [J/s] = [W] e-6 = [MW] | [26] |  | c_waterpump | 4 | 4 | $/kW | circulating water pumps | [3], Case B11A, B12A |  | Average Operating Values | 104.3 | 2824.1 | 2279.6 | 80.7 | 89.9444 | 523.8 | 11.572 | 0.088562 | 12.83 | 0.37726 |  | [29]
| power | 512.0803 | MW output | summation of the steam pump aux power consumption and power output from each turbine | [26] |  | c_wateraux | 28 | 27 | $/kW | circulating water system auxiliaries | [3], Case B11A, B12A |  | Average Deviations (%) | -25.5% | 18.6% | 11% | -6.1% | -20.7% | -2.8% | -11.1% | -2.8% |  |  |  | [29]
Inputs to Parameters Tab | steam_eff | 0.35811 | [0 -1] | the efficiency of the discharge cycle is P_out / Q_in |  |  | c_waterpipe | 22 | 21 | $/kW | circulating water piping | [3], Case B11A, B12A | 120-125 MW | Average Design Values | 120.6 | 2395.4 | 2063.4 | 86.15 | 104.1111 | 537.4 | 12.739 | 0.092228 | 12.21 | 0.41679 |  | [29]
| Q_s | 3405.9965 | MJ/tonne | enthalpy change of the steam converted to MJ/tonne |  |  | c_makeupwater | 5 | 5 | $/kW | make-up water system | [3], Case B11A, B12A |  | Average Operating Values | 93.2 | 2921.9 | 2333.9 | 80.09 | 83.5278 | 526.3 | 10.6502 | 0.089281 | 12.21 | 0.36848 |  | [29]
| deltaT_A | 25 | K | Temperature difference of two streams (steam and salt flows) at at end A in countercurrent heat exchanger |  |  | c_coolingwater | 3 | 3 | $/kW | component cooling water system | [3], Case B11A, B12A |  | Average Deviations (%) | -22.8% | 18.5% | 11.5% | -5.4% | -20.2% | -2% | -18.6% | -2.1% |  | 7478.2609 |  | [29]
| deltaT_B | 240 | K | Temperature difference between two streams (steam and salt flows) at end B in countercurrent heat exchanger |  |  | c_waterfoundation | 3 | 3 | $/kW | circulating water system foundations | [3], Case B11A, B12A | 100-110 MW | Average Design Values | 108.1 | 2434.9 | 2138.7 | 86.94 | 95.7778 | 537.5 | 12.4252 | 0.091348 | 13.1 | 0.40211 |  | [29]
[7 empty] | c_generator | 9 | 9 | $/kW | Generator equipment | [3], Case B11A, B12A |  | Average Operating Values | 90.2 | 3016.8 | 2418.3 | 80.26 | 81.4722 | 532.1 | 11.1307 | 0.085709 | 13.1 | 0.35562 |  | [29]
[7 empty] | c_stationservice | 10 | 10 | $/kW | station service equipment | [3], Case B11A, B12A |  | Average Deviations (%) | 17% | -19% | -10.3% | 5.8% | 14.2% | 0.1% | 8.6% | 4.5% |  |  |  | [29]
[7 empty] | c_switchgear | 18 | 17 | $/kW | switchgear & motor control | [3], Case B11A, B12A
[7 empty] | c_conduit | 8 | 7 | $/kW | conduit and cable tray | [3], Case B11A, B12A
[7 empty] | c_wirescables | 14 | 14 | $/kW | wire and cable | [3], Case B11A, B12A
[7 empty] | c_protection | 1 | 1 | $/kW | protective equipment | [3], Case B11A, B12A
[7 empty] | c_standby | 3 | 3 | $/kW | standby equipment | [3], Case B11A, B12A
[7 empty] | c_powertransformers | 14 | 14 | $/kW | main power transformers | [3], Case B11A, B12A
[7 empty] | c_electricalfoundation | 2 | 2 | $/kW | electrical foundations | [3], Case B11A, B12A
[7 empty] | c_steamturbinecontrols | 1 | 1 | $/kW | steam turbine control equipment | [3], Case B11A, B12A
[7 empty] | land_cost | 1 | 1 | $/kW | Land cost (owner costs) | [3], Case B11A, B12A
[7 empty] | FOM_labor | 68.101 | 70.57 | $/kWnet | includes annula operating labor, maintenance labor, administrative and support labor, property taxes and insurance | [3], Case B11A, B12A
[7 empty] | VOM_water | 0.56869 | 0.53092 | $/MWh-net | water costs | [3], Case B11A, B12A
[7 empty] | VOM_wastewater | 0.48038 | 0.45781 | $/MWh-net | wastewater treatment costs | [3], Case B11A, B12A
[7 empty] | decomissioning_cost | 0.29 to 0.36 | 0.29 to 0.36 | INR CR per MW | they include: Employee costs, station overhead, O&M expenses, pre-demolition costs: environmental remediation (asbestos cleanup), demolition costs (including scrap removal), coal combustion residuals, coal storage area clean up (Shrimali TN paper) | Shrimali
Calculations
[7 empty] | P_aux | 0.38574 | 0.38686 | % | additional percentage (of total MW output) that is auxiliary consumption for the molten salt retrofit system
[7 empty] | FOM | 68101 | 70570 | $/MW | total fixed operating and maintenance costs (labor estimate, U.S. base is $38.50 / hour )
[7 empty] | VOM | 1.0491 | 0.98873 | $/MWh-net | variable operating costs associated with water
[7 empty] | Capex | 589000 | 607000 | $/MW | capital cost of steam turbine system and additional upgrades. This does not include the cost of buildings / enclosures

## BESS
Description | 2020 values | 2030 values | 2050 values | Units | Source | Uncertainties | unit amount | Conversion rate | unit | Source
Inverter lifetime (years) | 16.7 | 22.5 | 25 | years | 31 |  | 1 crore INR | 121400 | USD | 32
Lifetime | 6000 | 8000 | 20000 | battery cycles | 31 |  | 1 USD | 82.3723 | INR | 32
charging efficinecy | 95 | 96 | 97 | % | 31
Depth of Discharge | 92 | 95 | 99 | % | 31
Discharge time | 2 | 4 | 10 | hours | 31
Capital costs | 288932 | 166318 | 132326 | $ / MWh | 31
capital costs power | 817022 | 469818 | 375126 | $ / MW | 31
Fixed OM | 9712 | 6070 | 0.04 | $ /MW /year | 31
Variable OM | 6070 |  |  | $/MWh | 31

## DecommissioningCosts
| Description | Value | Units | Source | Note
cost | Employee Costs | 7.11 | $M/1000 MW | 30 | check: does it make sense to exclude these costs from the repurposing option? (Yes, but this source is not a very good source imo)
cost | Station overheads | 24.14 | $M/1000 MW | 30
cost | O&M expenses | 3.9 | $M/1000 MW | 30
cost | Pre-demolition costs: environmental regulation | 0.09 | $M/1000 MW | 30
cost | Demolition costs | 4.05 | $M/1000 MW | 30
cost | Coal combustion residuals | 15.72 | $M/1000 MW | 30
cost | Coal storage area cleanup | 3.1 | $M/1000 MW | 30
benefit | scrap value | 65.65 | $M/1000 MW | 30
benefit | land utilization | 9.07 | $M/1000 MW | 30
benefit | equipment (switchyard, substation) | 16.4 | $M/1000 MW | 30
benefit | remediation | 15.72 | $M/1000 MW | 30
benefit | transmission and interconnection evacuation | 15.96 | $M/1000 MW | 30
| total decomission cost | 58.11 | $M/1000 MW | 30
57.15

## AspenInputs_Operating
Variable Name | Units | Description | 700MW | 600MW | 660MW | 500MW | 250MW | 210MW | 195_200MW | 140MW | 120_125MW | 100_110MW | Trombay
P_out | MW | Average Operating Values or design values | 685 | 600 | 650 | 446.3 | 251.3 | 198.5 | 166.2 | 104.3 | 93.2 | 90.2 | 500
steam_eff | [0 - 1] | steam turbine efficiency (not the full plant efficiency, which is around 38.6 to 40.1 % for the best) | 0.48 | 0.463 | 0.463 | 0.408 | 0.384 | 0.388 | 0.363 | 0.377 | 0.368 | 0.356
P_aux_TES | MW | Aux Power Consumption for TES | 2.6423 | 2.3144 | 2.5146 | 1.7266 | 0.97218 | 0.76792 | 0.64296 | 0.4035 | 0.36055 | 0.34895
P_aux_coal | MW | Aux Power Consumption for Coal | 35 | 24 | 26.7 | 34.9899 | 23.7227 | 18.9965 | 17.0189 | 13.3817 | 11.3797 | 11.8162
F_steam | kg/s | Flow rate of main steam | 510 | 440 | 480 | 370.2222 | 216.83 | 174.06 | 150.53 | 89.94 | 83.53 | 81.47
Pressure_steam | bar | pressure of main steam | 242 | 166.5 | 166.5 | 160 | 148 | 132 | 107 | 116 | 107 | 111
Temperature_steam | C | peak steam temperature | 560 | 560 | 560 | 539.2 | 537 | 535 | 532.8 | 523.8 | 526.3 | 532.1
Notes_Sources |  |  | [3] | [3] | [3] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5]
|  | deseing eff | 0.48 | 0.463 | 0.463 | 0.43535 | 0.42931 | 0.42479 | 0.41939 | 0.4189 | 0.41699 | 0.40231
|  | Capacity range of units | No. of units | Average Design | Average Operating | Average | Range of operating THR
|  |  |  | Turbine Heat Rate | Turbine Heat Rate | Deviation (%)
|  |  |  | (kcal/kWh)* | (kcal/kWh)*
|  | 100-110 MW | 8 | 2134.4 | 2356.3 | 10.4 | 2215 - 2881 | 36.52% | 1/(capacity_op_df.loc[i,'TurbineHeatRate']/860.421)
|  | 120-125 MW | 9 | 2081 | 2314.6 | 11.2 | 2162 - 2796 | 37.17%
|  | 140 MW | 4 | 2054 | 2279.4 | 11 | 2243 - 2325 | 37.75%
|  | 195-200 MW | 5 | 2051.9 | 2305.8 | 12.4 | 2033 - 2893 | 37.32%
|  | 210 MW | 49 | 2024.3 | 2166.1 | 7 | 2045 - 2442 | 39.72%
|  | 250 MW | 5 | 2001.2 | 2239.2 | 11.9 | 2179 - 2274 | 38.43%
|  | 500 MW | 5 | 1976.4 | 2108.3 | 6.7 | 2087 - 2179 | 40.81%

## AspenInputs
Variable Name | Units | Description | 700MW | 600MW | 660MW | 500MW | 250MW | 210MW | 195_200MW | 140MW | 120_125MW | 100_110MW
P_out | MW | Average Operating Values or design values | 685 | 600 | 650 | 500 | 250 | 210.1 | 199 | 140.1 | 120.6 | 108.1
steam_eff | [0 - 1] | steam turbine efficiency (not the full plant efficiency, which is around 38.6 to 40.1 % for the best) | 0.48 | 0.463 | 0.463 | 0.43535 | 0.42931 | 0.42479 | 0.41939 | 0.4189 | 0.41699 | 0.40231
P_aux_TES | MW | Aux Power Consumption for TES | 2.64 | 2.31 | 2.51 | 1.9345 | 0.96725 | 0.81288 | 0.76993 | 0.54205 | 0.4666 | 0.41824
P_aux_coal | MW | Aux Power Consumption for Coal | 35 | 24 | 26.7 | 39.2 | 23.6 | 19 | 17.02 | 13.38 | 11.38 | 11.82
F_steam | kg/s | Flow rate of main steam | 510 | 440 | 480 | 421.6111 | 207.8611 | 179.1944 | 178.4167 | 113.5833 | 104.1111 | 95.7778
Pressure_steam | bar | pressure of main steam | 242 | 166.5 | 166.5 | 167.9873 | 147.6876 | 139.45 | 133.0757 | 130.2318 | 127.3879 | 124.2498
Temperature_steam | C | peak steam temperature | 560 | 560 | 560 | 537.6 | 537.6 | 537.3 | 538 | 539 | 537.4 | 537.5
Notes_Sources |  |  | [3] | [3] | [3] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5]

## AspenInputs_2
Variable Name | Units | Description | 700MW | 600MW | 660MW | 500MW | 250MW | 210MW | 195_200MW | 140MW | 120_125MW | 100_110MW | 500MW_0 | 500MW_1 | 500MW_2 | 500MW_3 | 500MW_4 | 250MW_0 | 250MW_1 | 250MW_2 | 250MW_3 | 250MW_4 | 210MW_0 | 210MW_1 | 210MW_2 | 210MW_3 | 210MW_4 | 210MW_5 | 210MW_6 | 210MW_7 | 210MW_8 | 210MW_9 | 210MW_10 | 210MW_11 | 210MW_12 | 210MW_13 | 210MW_14 | 210MW_15 | 210MW_16 | 210MW_17 | 210MW_18 | 210MW_19 | 210MW_20 | 210MW_21 | 210MW_22 | 210MW_23 | 210MW_24 | 210MW_25 | 210MW_26 | 210MW_27 | 210MW_28 | 210MW_29 | 210MW_30 | 210MW_31 | 210MW_32 | 210MW_33 | 210MW_34 | 210MW_35 | 210MW_36 | 210MW_37 | 210MW_38 | 210MW_39 | 210MW_40 | 210MW_41 | 210MW_42 | 210MW_43 | 210MW_44 | 210MW_45 | 210MW_46 | 210MW_47 | 210MW_48 | 195_200MW_0 | 195_200MW_1 | 195_200MW_2 | 195_200MW_3 | 195_200MW_4 | 140MW_0 | 140MW_1 | 140MW_2 | 140MW_3 | 120_125MW_0 | 120_125MW_1 | 120_125MW_2 | 120_125MW_3 | 120_125MW_4 | 120_125MW_5 | 120_125MW_6 | 120_125MW_7 | 120_125MW_8 | 100_110MW_0 | 100_110MW_1 | 100_110MW_2 | 100_110MW_3 | 100_110MW_4 | 100_110MW_5 | 100_110MW_6 | 100_110MW_7
P_out | MW | Average Operating Values or design values | 685 | 600 | 650 | 500 | 250 | 210.1 | 199 | 140.1 | 120.6 | 108.1 | 500 | 500 | 500 | 500 | 500.21 | 250 | 250 | 250 | 250 | 250 | 210 | 210.2 | 210 | 210.4 | 210 | 210 | 210 | 210.4 | 210 | 210.42 | 210.36 | 210 | 210 | 210 | 210 | 210 | 210.5 | 210 | 210 | 210 | 210 | 210 | 210 | 210.18 | 210 | 210 | 210.56 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210.52 | 210 | 210 | 210 | 210.42 | 210.36 | 210 | 210 | 210 | 210 | 195 | 200 | 200.09 | 200 | 200.09 | 140 | 140 | 140.23 | 140 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120.3 | 125 | 100 | 105 | 110 | 110 | 110 | 110 | 110 | 110
steam_eff | [0 - 1] | steam turbine efficiency (not the full plant efficiency, which is around 38.6 to 40.1 % for the best) | 0.48 | 0.463 | 0.463 | 0.43535 | 0.42931 | 0.42479 | 0.41939 | 0.4189 | 0.41699 | 0.40231 | 0.43632 | 0.43632 | 0.43632 | 0.43361 | 0.43416 | 0.42931 | 0.42935 | 0.42914 | 0.42935 | 0.42935 | 0.42862 | 0.42862 | 0.41727 | 0.42854 | 0.42871 | 0.42871 | 0.42871 | 0.41627 | 0.41526 | 0.42871 | 0.42978 | 0.42095 | 0.41625 | 0.41627 | 0.42871 | 0.43146 | 0.42871 | 0.43129 | 0.41627 | 0.41627 | 0.42871 | 0.42871 | 0.41768 | 0.42178 | 0.42178 | 0.42178 | 0.42871 | 0.42021 | 0.4275 | 0.42833 | 0.43216 | 0.42871 | 0.42871 | 0.42867 | 0.42867 | 0.42871 | 0.42871 | 0.41727 | 0.41768 | 0.42897 | 0.42897 | 0.41727 | 0.43151 | 0.42871 | 0.42871 | 0.42871 | 0.43429 | 0.41723 | 0.41671 | 0.43021 | 0.41627 | 0.41627 | 0.41727 | 0.41727 | 0.4189 | 0.4189 | 0.4189 | 0.4189 | 0.41876 | 0.41876 | 0.40972 | 0.40972 | 0.40972 | 0.40972 | 0.40972 | 0.40972 | 0.42553 | 0.40244 | 0.40207 | 0.40244 | 0.40586 | 0.40586 | 0.40207 | 0.40207 | 0.40207
P_aux_TES | MW | Aux Power Consumption for TES | 2.64 | 2.31 | 2.51 | 1.9345 | 0.96725 | 0.81288 | 0.76993 | 0.54205 | 0.4666 | 0.41824 | 1.9345 | 1.9345 | 1.9345 | 1.9345 | 1.9353 | 0.96725 | 0.96725 | 0.96725 | 0.96725 | 0.96725 | 0.81249 | 0.81326 | 0.81249 | 0.81404 | 0.81249 | 0.81249 | 0.81249 | 0.81404 | 0.81249 | 0.81411 | 0.81388 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81442 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81319 | 0.81249 | 0.81249 | 0.81466 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.8145 | 0.81249 | 0.81249 | 0.81249 | 0.81411 | 0.81388 | 0.81249 | 0.81249 | 0.81249 | 0.81249 | 0.75446 | 0.7738 | 0.77415 | 0.7738 | 0.77415 | 0.54166 | 0.54166 | 0.54255 | 0.54166 | 0.46428 | 0.46428 | 0.46428 | 0.46428 | 0.46428 | 0.46428 | 0.46428 | 0.46544 | 0.48363 | 0.3869 | 0.40625 | 0.42559 | 0.42559 | 0.42559 | 0.42559 | 0.42559 | 0.42559
P_aux_coal | MW | Aux Power Consumption for Coal | 35 | 24 | 26.7 | 39.2 | 23.6 | 19 | 17.02 | 13.38 | 11.38 | 11.82 | 43.45 | 38.55 | 39.05 | 37.55 | 37.5157 | 23.95 | 25.1 | 21.35 | 23.325 | 24.325 | 20.475 | 23.7316 | 18.732 | 17.905 | 20.37 | 20.727 | 21.105 | 19.988 | 23.499 | 20.4107 | 24.8646 | 19.131 | 18.942 | 18.69 | 19.572 | 18.669 | 17.0505 | 17.409 | 19.152 | 18.963 | 20.37 | 19.299 | 19.803 | 20.8499 | 19.908 | 27.027 | 22.6141 | 18.9 | 21.105 | 21.924 | 21.84 | 21.798 | 18.9 | 19.467 | 19.215 | 19.95 | 19.257 | 19.152 | 18.186 | 20.5889 | 18.732 | 16.947 | 20.097 | 19.3586 | 20.5311 | 19.467 | 18.438 | 18.228 | 23.415 | 19.5 | 17.6 | 16.1473 | 25.18 | 23.4906 | 19.18 | 19.782 | 20.4175 | 12.474 | 12.024 | 16.164 | 12.432 | 17.184 | 16.392 | 12.648 | 14.892 | 16.3247 | 14.375 | 19.76 | 14.847 | 16.841 | 10.56 | 10.021 | 10.318 | 14.344 | 15.884
F_steam | kg/s | Flow rate of main steam | 510 | 440 | 480 | 421.6111 | 207.8611 | 179.1944 | 178.4167 | 113.5833 | 104.1111 | 95.7778 | 423.3333 | 423.3333 | 423.3333 | 418.8333 | 419.1667 | 211.1111 | 211.1111 | 205.5556 | 205.8056 | 205.7778 | 177.7778 | 179.4444 | 186.9444 | 175 | 175 | 173.6111 | 175 | 188.3333 | 179.1667 | 175.5556 | 175 | 191.6667 | 188.3333 | 188.8889 | 176.3889 | 176.3889 | 176.3889 | 175.2778 | 179.4444 | 181.1111 | 175 | 174.4444 | 180.5556 | 181.1111 | 186.1111 | 186.1111 | 176.3889 | 186.1111 | 178.3056 | 182.5 | 179.1667 | 176.6667 | 176.3889 | 173.6111 | 173.6111 | 175 | 175.2778 | 180.5556 | 186.1111 | 177.7778 | 177.7778 | 181.3889 | 176.3889 | 175.5556 | 175 | 175 | 177.7778 | 183.3333 | 182.6389 | 162.0833 | 177.2222 | 175 | 188.8889 | 188.8889 | 114.4444 | 109.7222 | 111.1111 | 119 | 100 | 100.5556 | 113.8889 | 100.5556 | 103.3333 | 102.7778 | 111.9444 | 95.5556 | 108.3333 | 116.6667 | 88.8889 | 90.5556 | 90 | 90 | 101.3889 | 98.3333 | 90.2778
Pressure_steam | bar | pressure of main steam | 242 | 166.5 | 166.5 | 167.9873 | 147.6876 | 139.45 | 133.0757 | 130.2318 | 127.3879 | 124.2498 | 166.7124 | 170.6351 | 166.7124 | 165.7318 | 169.9486 | 147.0992 | 147.0992 | 149.0605 | 144.1572 | 151.1199 | 144.1572 | 144.1572 | 127.486 | 147.0992 | 147.0992 | 144.1572 | 147.0992 | 126.5053 | 134.3506 | 147.0992 | 147.0992 | 132.3893 | 126.5053 | 126.5053 | 144.1572 | 147.0992 | 144.1572 | 143.1766 | 120.6213 | 124.544 | 147.0992 | 147.0992 | 127.486 | 127.486 | 127.486 | 134.3506 | 147.0992 | 127.486 | 147.0992 | 147.0992 | 147.0992 | 147.0992 | 147.0992 | 144.1572 | 144.1572 | 144.1572 | 144.2553 | 133.3699 | 133.3699 | 144.1572 | 144.2553 | 127.486 | 147.0992 | 147.0992 | 147.0992 | 147.0992 | 147.0992 | 125.0343 | 127.486 | 144.2553 | 130.428 | 124.544 | 132.6835 | 133.3699 | 127.486 | 127.486 | 127.486 | 138.2733 | 127.8782 | 127.486 | 126.3092 | 127.486 | 124.544 | 125.1324 | 130.428 | 127.486 | 129.4473 | 88.2595 | 127.8782 | 127.486 | 126.5053 | 136.3119 | 134.8409 | 125.5247 | 127.486
Temperature_steam | C | peak steam temperature | 593 | 566 | 566 | 537.6 | 537.6 | 537.3 | 538 | 539 | 537.4 | 537.5 | 537 | 538 | 537 | 538 | 538 | 537 | 537 | 537 | 537 | 540 | 540 | 537 | 540 | 539 | 540 | 535 | 540 | 535 | 540 | 540 | 540 | 540 | 540 | 540 | 535 | 540 | 540 | 540 | 535 | 535 | 540 | 535 | 535 | 535 | 535 | 535 | 535 | 540 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 535 | 540 | 540 | 539 | 535 | 535 | 535 | 540 | 540 | 540 | 537 | 535 | 535 | 540 | 535 | 535 | 540 | 540 | 538 | 540 | 535 | 543 | 540 | 535 | 537 | 535 | 537 | 537.8 | 540 | 535 | 540 | 535 | 535 | 535 | 540 | 540 | 540 | 535 | 540
Notes_Sources |  |  | [3] | [3] | [3] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | [4],[5] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## AspenInputs_500MW
Variable Name | Units | Description | 500MW_0 | 500MW_1 | 500MW_2 | 500MW_3 | 500MW_4
P_out | MW | Average Operating Values or design values | 500 | 500 | 500 | 500 | 500.21
steam_eff | [0 - 1] | steam turbine efficiency (not the full plant efficiency, which is around 38.6 to 40.1 % for the best) | 0.43632 | 0.43632 | 0.43632 | 0.43361 | 0.43416
P_aux_TES | MW | Aux Power Consumption for TES | 1.9345 | 1.9345 | 1.9345 | 1.9345 | 1.9353
P_aux_coal | MW | Aux Power Consumption for Coal | 43.45 | 38.55 | 39.05 | 37.55 | 37.5157
F_steam | kg/s | Flow rate of main steam | 423.3333 | 423.3333 | 423.3333 | 418.8333 | 419.1667
Pressure_steam | bar | pressure of main steam | 166.7124 | 170.6351 | 166.7124 | 165.7318 | 169.9486
Temperature_steam | C | peak steam temperature | 537 | 538 | 537 | 538 | 538
Notes_Sources |  |  | 0 | 0 | 0 | 0 | 0

## Qualitative Assumptions
Constraints | Assumption | Source ID
Heat Exchanger Balance
Price Profile Input
salt pumps are not a driving capital cost and a linearized equation is used to estimate the unit cost of the pumps
Salt corrosion and replacement rates are not incluced, usually not a problem within the 25-30 year lifetime of the facility |  | 15
Assuming operating conditions (not design values) for most units except those that are 600 MW + because these are typically newer and more efficiently operated
ancillary services (inertia value) is not included because this is currently inconsistently valued, and the value changes as more renewables come online | system-level benefits will be analyzed separately
uncertainties on the heat exchanger costs due to scale | there have been demonstration projects (MIT has one) but these are small, resarch stage, expensive

## GenX_sources
| lifetime | average_cap | CRF | Profits_TES | chargeMW_investment | dischargeMW_investment | energy_MWh_investment | discharge MW with upgrade | discharge MW with upgrade and CRF
Coal Plant TES Retrofit Type in Uttar Pradesh | remaining lifetime of the coal plant based on 50 year lifetime assumption. This is the lifetime over which the TES would operate. | average capacity of the cluster in MW | Capital Recovery Factor of the unit, based on age of the coal plant | Objective function of the TES dispatch and sizing optimization (negative values are annual profit. Positive values indicate an annual loss) | USD per MW of installed charging capacity. Includes charger and cold salt pumps. Does not use CRF | USD per MW of discharging capacity. Includes heat exchanger, hot salt pumps, does not use CRF | USD per MWh (thermal) installed. Includes cost of tank and energy storage medium, does not use CRF | USD per MW of installed charging capacity, same as before but includes an upgrade cost for the steam turbine | USD per MW of installed charging capacity, same as before but includes an upgrade cost for the steam turbine and multiplied by the CRF. | BESS $/kW - yr from the same source as TES power cycle upgrade costs | Factor to take out the labor costs
0 | 3 | 54.6961 | 0.3951 | 2481.8875 | 5760.7614 | 56662.1971 | 20226.8202 | 422893.1971 | 167085.1022 | 333.8595 | 0.20967
1 | 1 | 108.242 | 1.09 | 15844.7815 | 4469.4413 | 44188.3687 | 20226.8202 | 410419.3687 | 447357.1118 | 921.05 | 0.076
2 | 6 | 123.5395 | 0.2229 | 1370.0232 | 3681.4294 | 42600.9897 | 20226.8202 | 408831.9897 | 91128.6505 | 188.3505 | 0.37165
3 | 7 | 54.6961 | 0.1987 | 414.714 | 3174.484 | 56662.1971 | 20226.8202 | 422893.1971 | 84028.8783 | 167.9015 | 0.41691
4 | 6 | 252.4005 | 0.2229 | 2292.2151 | 2740.8842 | 34064.7071 | 20226.8202 | 400295.7071 | 89225.9131 | 188.3505 | 0.37165
5 | 16 | 91.1602 | 0.1203 | -2161.1259 | 2538.4397 | 46787.6643 | 20226.8202 | 413018.6643 | 49686.1453 | 101.6535 | 0.68861
6 | 25 | 91.1602 | 0.1018 | -2843.9734 | 2528.8575 | 46787.6643 | 20226.8202 | 413018.6643 | 42045.3 | 86.021 | 0.81375
7 | 25 | 91.1602 | 0.1018 | -2843.9734 | 2528.8575 | 46787.6643 | 20226.8202 | 413018.6643 | 42045.3 | 86.021 | 0.81375
8 | 30 | 91.1602 | 0.0973 | -3046.472 | 2491.5093 | 46787.6643 | 20226.8202 | 413018.6643 | 40186.716 | 82.2185 | 0.85139
9 | 11 | 229.4305 | 0.1469 | -3190.8534 | 2330.2721 | 34384.6424 | 20226.8202 | 400615.6424 | 58850.4379 | 124.1305 | 0.56392
10 | 25 | 198.4436 | 0.1018 | -6195.5545 | 2330.2721 | 35737.3461 | 20226.8202 | 401968.3461 | 40920.3776 | 86.021 | 0.81375
11 | 18 | 229.4305 | 0.1142 | -5978.557 | 2330.2721 | 34384.6424 | 20226.8202 | 400615.6424 | 45750.3064 | 96.499 | 0.7254
12 | 25 | 229.4305 | 0.1018 | -7076.3644 | 2330.2721 | 34384.6424 | 20226.8202 | 400615.6424 | 40782.6724 | 86.021 | 0.81375
13 | 28 | 275.911 | 0.0989 | -8471.2112 | 2330.2721 | 32690.564 | 20226.8202 | 398921.564 | 39453.3427 | 83.5705 | 0.83762
14 | 31 | 275.911 | 0.0967 | -8701.9766 | 2330.2721 | 32690.564 | 20226.8202 | 398921.564 | 38575.7152 | 81.7115 | 0.85667
15 | 30 | 275.911 | 0.0973 | -8639.2058 | 2330.2721 | 32690.564 | 20226.8202 | 398921.564 | 38815.0682 | 82.2185 | 0.85139
16 | 12 | 487.9744 | 0.1397 | -5556.9161 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 55008.0212 | 118.0465 | 0.59299
17 | 28 | 487.9744 | 0.0989 | -11846.9384 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 38942.6864 | 83.5705 | 0.83762
18 | 23 | 487.9744 | 0.1044 | -10999.4511 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 41108.3565 | 88.218 | 0.79349
19 | 31 | 487.9744 | 0.0967 | -12200.2966 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 38076.4184 | 81.7115 | 0.85667
20 | 29 | 487.9744 | 0.0981 | -11967.1487 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 38627.6799 | 82.8945 | 0.84445
21 | 24 | 487.9744 | 0.103 | -11216.6801 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 40557.0951 | 87.035 | 0.80427
22 | 35 | 487.9744 | 0.0946 | -12527.5518 | 2330.2721 | 27527.2045 | 20226.8202 | 393758.2045 | 37249.5261 | 79.937 | 0.87569
23 | 34 | 551.6464 | 0.0951 | -12912.1002 | 2330.2721 | 32780.708 | 20226.8202 | 399011.708 | 37946.0134 | 80.3595 | 0.87109
24 | 30 | 551.6464 | 0.0973 | -12522.9002 | 2330.2721 | 32780.708 | 20226.8202 | 399011.708 | 38823.8392 | 82.2185 | 0.85139
25 | 35 | 551.6464 | 0.0946 | -13318.2094 | 2330.2721 | 32780.708 | 20226.8202 | 399011.708 | 37746.5076 | 79.937 | 0.87569
averages of profitable runs |  |  | 0.10482 |  | 2366.7757 | 34054.5799 | 20226.8202 | 400285.5799 | 41961.7869 |  | 0.80159
Comparisions | $50 - $100 / kW yr for Li-ion | given by Yifu |  |  | 248.0832 | 3569.5686 | 2120.156
greenfield discharge investment in U.S., with labor costs | 366231 | $/MW, so $97/kW |  |  | $0.2/kW yr | $3.5 / kWyr | $2/kWyr |  | $40/kWyr
BESS in the same report | 845 | $/kW
factor to compare with Li-ion | 1
percentage of upgrade (assumes 30% of the equipment in the power cycle needs replacement) | 0.3
factor to use in Upgrade Costs tab | 0.3

## GenX
| Existing_Cap_MW | Existing_Cap_MWh | Existing_Charge_Cap_MW | Inv_Cost_per_MWyr | Inv_Cost_per_MWhyr | Inv_Cost_Charge_per_MWyr | Fixed_OM_Cost_per_MWhyr | Fixed_OM_Cost_charge_per_MWyr | Max_Cap_MW | Max_Cap_MWh | Max_Charge_Cap_MW | Var_OM_Cost_per_MWh_In | Cap_Size | Start_Cost_per_MW | Up_Time | Down_Time | Ramp_Up_Percentage | Ramp_Dn_Percentage | Self_Disch | Eff_Up | Eff_Down
GenX Description | The existing capacity of a power plant in MW. | The existing capacity of storage in MWh where STOR = 1 or STOR = 2. | The existing charging capacity for resources where STOR = 2. | Annualized capacity investment cost of a technology (/MW/year). | Annualized investment cost of the energy capacity for a storage technology (/MW/year), applicable to either STOR = 1 or STOR = 2. | Annualized capacity investment cost for the charging portion of a storage technology with STOR = 2 (/MW/year). | Fixed operations and maintenance cost of the energy component of a storage technology (/MWh/year). | Fixed operations and maintenance cost of the charging component of a storage technology of type STOR = 2. | -1 (default) – no limit on maximum discharge capacity of the resource. If non-negative, represents maximum allowed discharge capacity (in MW) of the resource. | -1 (default) – no limit on maximum energy capacity of the resource. If non-negative, represents maximum allowed energy capacity (in MWh) of the resource with STOR = 1 or STOR = 2. | -1 (default) – no limit on maximum charge capacity of the resource. If non-negative, represents maximum allowed charge capacity (in MW) of the resource with STOR = 2. | Variable operations and maintenance cost of the charging aspect of a storage technology with STOR = 2, or variable operations and maintenance costs associated with flexible demand deferral with FLEX = 1. Otherwise 0 (/MWh). | Size (MW) of a single generating unit. This is used only for resources with integer unit commitment (THERM = 1) - not relevant for other resources. | Cost per MW of nameplate capacity to start a generator (/MW per start). Multiplied by the number of generation units (each with a pre-specified nameplate capacity) that is turned on. | Minimum amount of time a resource has to stay in the committed state. | Minimum amount of time a resource has to remain in the shutdown state. | [0,1], Maximum increase in power output from between two periods (typically hours), reported as a fraction of nameplate capacity. Applies to thermal plants, and reservoir hydro resource (HYDRO = 1). | 0,1], Maximum decrease in power output from between two periods (typically hours), reported as a fraction of nameplate capacity. Applies to thermal plants, and reservoir hydro resource (HYDRO = 1). | [0,1], The power loss of storage technologies per hour (fraction loss per hour)- only applies to storage techs. | [0,1], Efficiency of charging storage – applies to storage technologies (all STOR types). | [0,1], Efficiency of discharging storage – applies to storage technologies (all STOR types).
Value | 0 | 0 | 0 | 3574 | 2120 | 248 | 0 | 0 |  | -1 |  | 0 |  | 10.15 | 0 | 0 | 0.5 | 0.5 | 0.00041667 | 0.95 | 0.35811
Calculation / Description | TES is not a generator | No existing TES | No existing TES | average annualized capacity investment cost per MW of discharge capacity, for the profitable units of a fleet analysis. Includes heat exchanger, hot salt pumps, any upgrade costs for the steam turbine | average annualized energy capacity investment cost, per MWh_th (thermal) storage for the profitable units of a fleet analysis. Includes cost of tank and energy storage medium | average annualized capacity investment costs per MW of charge capacity for the profitable units of a fleet analysis. Includes charger and cold salt pumps. |  |  | Change to the existing capacity of coal plants | Potentially limited by land use | Change to the existing capacity of coal plants |  | Change to size of the coal plant units
Sources |  |  |  | 10x difference

## Sources
Source ID | Citation |  | Notes
1 | Chernyakhovskiy, Ilya, Mohit Joshi, David Palchak and Amy Rose. 2021. Energy Storage in South Asia: Understanding the Role of Grid-Connected Energy Storage in South Asia’s Power Sector Transformation. Golden, CO: National Renewable Energy Laboratory. NREL/TP-6A20-79915. https://www.nrel.gov/docs/fy21osti/79915.pdf. | https://www.nrel.gov/docs/fy21osti/79915.pdf | Inputs from NREL 2030 Baseline Marginal Cost, shared by authors. Request access: https://www.nrel.gov/analysis/reeds/request-access-form.html
2 | IEX
3 | NETL
4 | Tata Power consultation
5 | CEA report, 85 pulverized
6 | https://www.mhi.co.jp/technology/review/pdf/e444/e444015.pdf | minpower | "To maintain this condition, a minimum amount of steam (about 15 to 20% of the rated amount) must continue to flow. The cost to maintain this flow of steam goes to waste."
7 | https://www.powermag.com/managing-minimum-load/
8 | https://www.nrel.gov/docs/fy12osti/55433.pdf | kumar | Table 1-3: Startup Fuel Input and Other Startup Costs Table 1-5: Typical Damage from Cycling
9 | Rhys Jacob, Wasim Saman, and Frank Bruno, , "Capital cost expenditure of high temperature latent and sensible thermal energy storage systems", AIP Conference Proceedings 1850, 080012 (2017) https://doi.org/10.1063/1.4984433
10 | https://www.mdpi.com/1996-1073/14/4/1197 | caraballo | Table 2: Properties of selected molten salt TES materials, density as a funciton of temperature (average density was used)
11 | https://www.nrel.gov/docs/fy12osti/53066.pdf | glatzmaier | Table 1: Component costs for direct, two-tank molten salt TES system (base case) (p.7) The components listed in Table 1 do not include the hot and cold tank salt pumps. The convention for power towers is to include the cold-tank pump with the receiver system and the hot-tank pump with the steam generation system.
12 | CEEW Trilemma report
13 | CEEW full dataset shared from Trilemma report
14 | Inflation calcs |  | https://www.inflationtool.com/us-dollar/2011-to-present-value
15 | https://www.davidpublisher.com/Public/uploads/Contribute/5c6f6c1253ec6.pdf | ladkany | Corrosion rates, design thickness of stainless steel and carbon steel, structural design of the tanks in detail
16 | https://linkinghub.elsevier.com/retrieve/pii/S2095809921000473 | ding
17 | https://www.kloecknermetals.com/blog/what-is-the-density-of-stainless-steel/#:~:text=Let's%20look%20at%20the%20two,about%207980%20kg%2Fm3. |  | density of stainless steels
18 | https://www.industrialmetalsupply.com/blog/carbon-steel-vs-stainless-steel#:~:text=The%20average%20Density%20of%20Carbon,is%20less%20than%20stainless%20steel.&text=Depending%20on%20grade%2C%20the%20coefficient,%2F%20(m%20%C2%B0C). |  | density of carbon steel
19 | https://inldigitallibrary.inl.gov/sites/sti/sti/5554590.pdf |  | Nuclear heat exchanger report
20 | https://link.springer.com/content/pdf/10.1007/s11081-019-09449-y.pdf | hamilton dispatch | for $/start of power cycle, table 3, costs are comparable to [8]
21 | https://www.in2013dollars.com/us/inflation/2010?amount=301693000 |  | inflation
22 | https://www.sciencedirect.com/science/article/pii/S0360544222009604 | gong | q loss Table 1: Parameters used in the study. The corresponding variables used in the description of the simulation are also indicated.
23 | https://www.nrel.gov/docs/fy06osti/40166.pdf |  | nrel doc on nitrate salt pumps
24 | https://info.ornl.gov/sites/publications/files/Pub62809.pdf | robb | head, Table 1: Summary of pumps developed during the ANP and MSR programs
25 | Future of energy storage report |  | chargers costs and charging efficiency, Table 4.3
26 | Aspen Models |  | github to aspen files and ipynb?
27 | https://tradingeconomics.com/india/inflation-cpi#:~:text=India%20Inflation%20Rate%20Eases%20Only,to%20market%20forecasts%20of%206.35%25. |  | inflation rate of india
28 | https://www.eia.gov/analysis/studies/powerplants/capitalcost/pdf/capital_cost_AEO2020.pdf |  | EIA capital cost estimates 2019
29 | https://cea.nic.in/wp-content/uploads/2020/04/report_85_pul_coal.pdf |  | CEA & GIZ report - used for aspen study. State and central gov ownership and operational plants across different states in 2008 | same as source [5]
30 | https://documents1.worldbank.org/curated/en/144181629878602689/pdf/Coal-Plant-Repurposing-for-Ageing-Coal-Fleets-in-Developing-Countries-Technical-Report.pdf |  | Table 2.1
31 | First India Technology report
32 | https://www.forbes.com/advisor/money-transfer/currency-converter/inr-usd/?amount=10000000
33 | Crescent Dunes sizing estimation through Google maps satellite view
34 | CSP flexibility - https://castalia-advisors.com/wp-content/uploads/2021/07/Flexibility-of-CSP-White-Paper.pdf | castalia